## Slide 1: Booster Bias Supply Upgrade
November 30th, 2011

## Slide 2
Three new Ferrite Bias Supplies Built
    Two are complete – for NOvA
        One is fully tested and operational
        The other runs but needs further troubleshooting for odd slewing problem
    Third one is 40% complete - Booster spare
        Finished in the next 3-4 weeks
There are 10 “Ling” MK I supplies that will need upgrading – Booster West Gallery only
    Replace main rectifier Transformer – marginal power rating for 15 Hz operation.
    Replace PVC SCR heat sinks – prone to LCW water leaks with any pressure surge.
    Upgrade can be done one at a time by changing out supply with spare.

## Slide 3: Ling transformer test, November 15th, 2011
2250A @ 1Hz
2250A @ 15Hz
Chart: Time
| 1140 | 1143 | 1450 | 1600
outer winding | 30.8 | 30.8 | 51.7 | 52.3
center winding | 30.9 | 30.9 | 57.1 | 57.9
upper core | 30.9 | 30.9 | 63.8 | 68
lower core | 29.2 | 29.2 | 64.9 | 70.3
Chart: Time
| 1610 | 1640 | 1700 | 1725
outer winding | 52.3 | 86.4 | 99.2 | 108.8
center winding | 57.9 | 100.7 | 113.8 | 115.5
upper core | 68 | 74.6 | 79.7 | 87
lower core | 70.3 | 75.5 | 80 | 87

## Slide 4: Ling transformer test, November 16th, 2011
2250A @ 15Hz
Chart: Time
| 845 | 848 | 930 | 1055 | 1155 | 1330 | 1437 | 1530 | 1600 | 1700
outer winding | 32 | 32 | 86.2 | 114 | 115 | 116.1 | 116.7 | 116.6 | 117.1 | 117.2
center winding | 31.8 | 31.8 | 91 | 116.2 | 99.1 | 98.6 | 99.5 | 102.2 | 102.1 | 103.6
upper core | 31.4 | 31.4 | 51.4 | 83.3 | 95.8 | 106.3 | 110.6 | 112.3 | 113.1 | 114.2
lower core | 29.5 | 29.5 | 46.6 | 79.5 | 94.7 | 108.3 | 113.9 | 116.2 | 117.3 | 118.7

## Slide 5: Ling transformer test, November 17th and 18th, 2011
2250A @ 15Hz with fans
2250A @ 15Hz with fans
and top plate lifted 3.5 inches
Chart: Time
| 1055 | 1215 | 1330 | 1430 | 1505 | 1700 | 1730
outer winding | 30.8 | 98.3 | 105.5 | 106.5 | 107.7 | 108.1 | 108.8
center winding | 30.2 | 86.3 | 90.4 | 92.8 | 94 | 94.6 | 95.2
upper core | 31.4 | 67 | 88.5 | 96.9 | 105 | 107.3 | 108.2
lower core | 29.5 | 62.2 | 85.5 | 96.2 | 106.9 | 109.9 | 111.2
Chart: Time
| 1000 | 1115 | 1150 | 1350 | 1450 | 1550 | 1740
outer winding | 30.8 | 93.3 | 101.6 | 107 | 107.1 | 107.5 | 107.6
center winding | 30.9 | 81.8 | 88.1 | 92.6 | 93.1 | 94.5 | 96.5
upper core | 31.2 | 63.2 | 75.2 | 98.2 | 103.6 | 106.7 | 109.2
lower core | 29.7 | 58.1 | 70.8 | 98.2 | 104.9 | 109.1 | 112.6

## Slide 6: MK I Bias Supply SCR Packages – PVC cased heat sinks

## Slide 7
New Style SCR Packages with Larger Transformer

## Slide 8
MK I Bias Supply
Main Rectifier Transformer

## Slide 9
MK I Bias Supply
SCR Packages with Main Rectifier Transformer - Behind

## Slide 10
Last transformer order was in 2007. The vender was NWL and they provided six units at a cost of $16,474 ea.
The expected lead time is 4-6 months so they should be sent out for bid ASAP.