## Slide 1: ACNET Alarms
Brian Hendricks
May 30, 2012

## Slide 2: Alarm Types
analog
  simple comparison to minimum and maximum values
    single set of limits
digital
  nominal and mask
  isAlarm = (reading & mask) != (nominal & mask)
  can have up to 32 alarm messages per device
    individual masks of bits in alarm

## Slide 3: Alarm Attributes
can be enabled/disabled
can generate beam aborts/inhibit
  abort capability can be bypassed
  abort capability is dependent on front end
can specify number of consecutive scans in alarm before making report (tries needed)
can specify that scan be made on a clock event (default is periodic)
can specify alarm text (supports formatting directives)
can specify that the alarm must be user acknowledged
can specify alarm annunciation (sound or speech)
can specify alarm help web page

## Slide 4: Message Path
front ends
  make periodic alarm scans
  push alarms to a central alarm server
    Event Report Packet (ERP) including raw reading value
alarm server
  receives front end alarm messages
  processes messages using device database information
  sends alarm messages via multicasts with sequence numbers
    Event Display Packet (EDP)
  clients can individually request all alarms or a range of sequence numbers

## Slide 5: Message Path (contd)
alarm daemon
  top level client
  receives multicasts from alarm server
  sends individual messages to connected clients
  implementations exist in C++, Python, and Java
alarm display
  configured by D6 program
    maps which alarm lists appear and where they appear
  allows user interaction

## Slide 6: Alarm Paths
Alarm Server
Front
End
Front
End
Front
End
Daemon
Daemon
Daemon
Client
Client
Client
Client
Client
Client
Notification
Server
(MONITR)
User
User
Alarm Logger
DB

## Slide 7: Alarm Groups
every device can be mapped to a single alarm group
each group has a single alarm concentrator device
  name of the group is this device
if any device in group goes into alarm, the concentrator device goes into alarm
an alarm concentrator device can be a member of another group
  supports a hierarchy of alarm groups
can group by any criteria desired
  location, device type, etc.

## Slide 8: Alarm Group View
D1
D2
D3
D4
D5
D6
C1
C2
D7
D8
C3

## Slide 9: Alarm Lists
device database lists
  used to control display of alarms
  default is to use the alarm list corresponding to the device’s front end
  configured by DABBEL
  a device can only appear in one list
user lists
  used to enable/disable alarms
  configured by users (usually operators) on page D59/D67
  a device can appear in multiple lists

## Slide 10: Individual Alarm Notification
primarily for systems without 24/7 coverage
configured on web page
  http://www-ad.fnal.gov/monitor/
multiple notification types
  email
  cell phone text message
  pager
can set minimum time between notifications
can be made acknowledgeable
  optional list of backup contacts if no acknowledge

## Slide 11: Alarm Log
maintained by alarm server
contains device, date, alarm type, alarm status, alarm text, alarm value
viewable by
  alarmLog ACL command
  Alarms Viewer app (D11)
  Operations Memopad “Alarms Viewer”
    http://www-bd.fnal.gov/cgi-mcr/alarms.pl

## Slide 12: Support Applications
alarm display (PA1661)
  automatically started with console (also D68)
alarm control (D59/D67)
  edit individual alarms
  edit user alarm lists
alarm screen setup (D6)
  configure alarm screen by alarm lists
front end device download list edit (D121)
multiple alarm list control (F30)

## Slide 13: Miscellaneous
alarm blocks are downloaded to front ends following a reboot
multiple alarm blocks
  support different alarm conditions for different machine states
  controlled by a state device

## Slide 14: Alarms Gotchas
DABBEL only sets analog alarm limits and digital alarm nominals/masks when creating a property
front end alarms are only accepted by the alarm server if the “is alarmer” node flag is set
alarms will only appear on the alarm display if an alarm list can be determined
  front end or device alarm list must be specified
  can be viewed using the unmapped devices command