## Slide 1: LCW Upgrades - Final
Booster RF Cavity LCW Isolation Valve Replacement.
  8 valves and unions previously replaced
  An additional 10 valves and unions were replaced during long shut-down. The remaining 20 will be replaced when possible - coordinate with cavity rework schedule.
    Remaining Stations: 9, 10, 11, 12, 13, 14, 15, 16, 17, 18
Booster Bus LCW Strainer and Isolation Valve Replacement.
  Remove existing Y-strainers and replace with basket strainers at wall opposite beamline. Replace isolation valves.
    Strainers at 6 locations were installed: 1, 3, 6, 7, 13, & 19
    Basket strainer and parts for the remaining 7 locations have been purchased and will be installed when possible.

## Slide 2: LCW Upgrades - Final
Old Valves at 03 & 04
New Valves at 03 & 04
Booster Cavity LCW Isolation Valve Replacement

## Slide 3: LCW Upgrades - Final
Old Strainer & Valves at 07
New Strainer and Valves at 07
Booster Cavity LCW Strainer & Isolation Valve Replacement

## Slide 4: LCW Upgrades - Final
Finish connection of LCW Return piping in East and West Booster Galleries to LCW Return piping at CUB.
  All work was completed at the end of August 2012
LCW Return Pump at CUB
  Remove northern most old, existing return pump, and install previously purchased pump, and relocate valves to allow return pump isolation.
  All work was completed early October 2012

## Slide 5: LCW Upgrades - Final
LCW Return Pump and LCW Return Piping at CUB

## Slide 6: LCW Upgrades - Final
  Install LCW Isolation Valves in CUB Utility Tunnel
  Work is complete
EDWA Magnets
  Repipe EDWA magnet coils in parallel instead of in series
  Work is complete
Remove LCW Piping for Long 13 New Absorber
  Remove sections of 95LCW piping and cap
  Remove sections of 55LCW Supply and Return
  Work is complete

## Slide 7: LCW Upgrades - Final
New Valve in LCW Return from Enclosure
New Valve in LCW Supply to Enclosure
LCW Enclosure Isolation Valves in CUB Utility Tunnel

## Slide 8: LCW Upgrades - Final
Removed 55 LCW and Capped 95 LCW
Removed 55 LCW and 95 LCW
Remove LCW Piping for Long 13 New Absorber

## Slide 9: LCW Upgrades - Final
Miscellaneous LCW Work
  Magnet bus hose fittings for drainage
  Repair Choke leaks and Choke Tubing
  Remove Candy Cane Stop-Cocks and plug
  Replace Long 3 LCW Hoses
  Replace 400 MeV LCW hoses up chute
  Install LCW bypasses at return valves in the Galleries
  Work above is complete

## Slide 10: LCW Upgrades - Final
Booster Refill, Leak Testing, Commissioning and Balancing
  Booster LCW has been refilled
  Leak checking complete (never really complete!)