From stephen@fnal.gov Wed Feb 18 10:58:04 2004

Date: Thu, 12 Feb 2004 07:25:01 -0600

From: Stephen Pordes <stephen@fnal.gov>

To: baumbaugh@fnal.gov, bhanna@fnal.gov, hendricks@fnal.gov, molson@fnal.gov,

steimel@fnal.gov, demaat <demaat@fnal.gov>, Bill_Haynes <haynes@fnal.gov>,

nickerbocker@fnal.gov

Cc: Jonathan Lewis <jdl@fnal.gov>, Paul Czarapata <pcceed@fnal.gov>,

Mike_Syphers <syphers@fnal.gov>, yarema <yarema@fnal.gov>

Subject: blm meeting issue summary..

BLM proposal presentation 02/10/04

present: Hanna, Steimel, Votava, Haynes, Hendricks, Demaat, Pordes, Baumbaugh,

Knickerbocker, Olson

Al presented his picture of the requirements and architecture of a

system that can be tested in july. His transparencies are in the BLM

topic in Instrumentation (Doc 992-v2): discussion is based on these.

General issues to be addressed are:

are there features that are not needed;

are there features that are missing;

are there architecture decisions that need to be changed;

Key aspects:

DIGITIZING AND ABORTS

Digitize at some rate - up to 1 MHz  - with 14 bit ADC -> all quantities

are then constructed from digitized data:

4 types of constructs for aborts:

single sample threshold, 2 running sum thresholds with different lengths,

1 time over threshold.

Multiplicity thresholds for each type of abort.

Individual channel masking for each type of abort.

Abort type available to concentrator.

MECHANICALS

Similar size crate as present.

Daughter cards carry two channels each.

Design will avoid requirements for massive uncabling to replace a card.

HV will be as present.

CONTROL AND COMMUNICATION

Assume ACNET interface initially at least by BPM controller.

Communication initially via External Device Bus to be able to interface

with current system (hardware and software).

Same set of data buffers as present plus deep turn-by-turn buffers.

PC104 buss, EZ80 CPU

Ethernet spigot for future.

Issues re DIGITIZING AND ABORTS

Do we need 4 abort types? Do we need 64 states?

Can the concentrator use the abort types? Should it be able to?

Issues re CONTROL AND COMMUNICATION

BPM controller to be ACNET interface

is ethernet appropriate?

(suggested that bill haynes and al agree on a high speed data link

hosted by the BPM controller)

how much memory needs to be reserved on the BPM controller?

will look to see if Power PC available on PC104

assembly language or C?

Issues re MECHANICAL

request for power switch at front

request for voltage test points

request for led indicators

insistence on robustness

=========================================================================

Stephen