## Slide 1: Substation L1/ MCC L1 Update
March 21st, 2012

## Slide 2: Current Location
Located in Alcove
Hydraulic Lift

## Slide 3: Equipment Layout

## Slide 4: Project Schedule

## Slide 5: Project Schedule
General Cleanup 2-3 weeks prior to shutdown of substation
Generator will arrive one week before shutdown (if used)
Temporary electrical power will be setup the weekend prior regardless of whether or not a generator is used
Office Lights
Office Receptacles
Security Camera
Fire Detection Panels
Emergency Lights
Exit Signs
Crane
Hydraulic Lift
Sanitary Lift Station
Overhead Door
What Will What Will Not
be Powered be Powered
Heat
Air Conditioning
All other MCC loads
Welding Receptacles
Hall Receptacles

## Slide 6: No Generator Plan
“Siphon” power from panel DHP-L2-2 or DHP-L3-4
Cable will be run in cable trays
  4 conductor 350 mcm cable is heavy (~7 lbs./ft.) and will need an open area to lay
  Use cable trays as much as possible for load wiring
    If on the floor, cable bridges will be used in walkways to prevent tripping
Setup temporary panel board(s)
Run cable to individual loads (DHP panels, MCC loads)
DHP panels will be locked out and tagged out
Group lockbox
MCC loads will have configuration control locks
  We will check current prior to using any MCC loads to ensure they will not trip off during operation
Schedule will be the same as the generator, except that we will have power all day

## Slide 7: No Generator Plan Pictures

## Slide 8: Substation L1
Contract awarded to Federal Pacific February 10th, 2012
Waiting for approval drawings
Cost: $164,853
Due By: June 20, 2012
Profibus Network
  Remote monitoring
  Remote operation
Replaceable trip units
  Allows for proper coordination of breakers
  Cost in the hundreds of dollars
Advanced Local Monitoring
  Current meter on primary switch
  Panel meter capable of power factor measurements, harmonics, etc.
Features of New Substation
Source: www.siemens.com

## Slide 9: Scheduling
One week install time
  May need to be 10-12 hour days to accomplish this
One day Riggers
  Crew of 6-8
One week of electricians
  Crew of 2

## Slide 10: MCC L1
Req. placed
Waiting for bids
Cost: ~ $50,000
Due By: August 1st, 2012
Siemens Tiastar Smart Start
  Profibus Network
  Remote/Local Monitoring
    FLA, under/over current, status messages, input/output data, on, off
  HMI/PLC used to control loads
    Used to monitor and control 4 WL breakers used in Substation L1
    This will require in house programming
Features of New MCC
Source: Siemens

## Slide 11: Scheduling
Will be installed when Substation L1 is installed
One day install time
  Budgeted two to be safe
Several loads will need to be powered when power is turned off
  Crane, Overhead Door, Lift Station, Sump Pumps, Hydraulic Lift
  Sump pumps will be handled by temporary sump pumps

## Slide 12: Installation Costs
1 Crew of Riggers (6-8 men)
  1 Day: $12k
1 Week of Electricians
  $100/manhour x 2 electricians x 40 hours = $8,000
  $100/manhour x 2 electricians x 40 hours + $150/manhour x 2 electricians x 20 hours= $14,000
Generator
  $5,400 For a Month Rental
  $2,000/day Diesel
  $1,400 For a Panelboard (x2-?)
  Several Hundred Feet of Cable to Individual Loads
House Power
  $1,400 For a Panelboard (x2-?)
  250 ft. of 4 Conductor 350 MCM Cable (In Storage, Unsure of length)
  Several Hundred Feet of Cable to Individual Loads
 | Cost
Generator | ~ 53k
No Generator | ~ 35k

## Slide 13: Commissioning
Visual Inspection
Hi-Pot
Disconnect panel boards from temporary power
Reconnect panel boards
DHP-L1-1 will be turned on first
  Fire alarms
  Lighting
  Etc.
DHP-L1-2
DHP-L1-3

## Slide 14: What Will Become of the Removed Equipment?
Transformer will be kept as a spare
  Currently have 1 spare for 8 transformers (5 – high rise, 3 – LINAC)
  Transformer will be examined to make sure it is in good working order
  Will be stored in Booster parking lot
  Will be placed on a truck the same day it is removed to avoid excess rigger fees
Breakers
  Will be rebuilt and tested
  Used as spares
Primary Switch
  Will be rebuilt and tested
  Used as a spare

## Slide 15: Future
Create Site Wide Monitoring Network
Intranet
LINAC
Profibus
Booster
Profibus
Cross Gallery
Profibus
LINAC Profibus Section 1 (This Install)
LINAC Profibus Section 2 (MCC L2) $65k
Booster Profibus West
(Specifications Written)
Booster Profibus East
(Specifications Written)
Substation CG-1
(Specification Written) $200k
PIP Project
PIP Project
PIP Project
PIP Project
????
Note: attempting to move
CG-1 budget to operations
cost

## Slide 16: Future
Costs
  MCC L2 ~ $65k
  CG-1 ~ $200k
Install Times
  MCC L2 ~ 2 Days Electricians, 1 Day Riggers
  CG-1 ~ 1 Week Electricians, 1 Day Riggers
Affected Entities
  MCC L2
    Chilled Water to Linac
    Heaters
    Sump Pump
    Air Compressors
  CG-1
    Main Control Room
    Cross Gallery Motor Control
    High Bay
    MAC Room
    Computer Room