## Slide 1: Diode Bridge
11 Legs built
  12 by the end of day
Boards are being stuffed
Support Frame is being worked on

## Slide 2: Water Cooled Resistor

## Slide 3: Controls
More complicated than expected
  Will not merely be plug and play with old system
Minor modifications required for step start cabinet
  Terminal blocks and wiring need to be added
  SEL relay needs to be programmed
  Add brass box

## Slide 4: Booster East Transformer
Currently working on cost estimates
  Reuse old switchgear vs. buy new
Reuse old will require sheet metal work and a custom throat
  Will also require a crane for when the switchgear is eventually replaced
  Need to measure to make sure the transformer and switchgear will fit on the pad nicely when a throat is attached
New Switchgear will require gear that is similar to the square d lineup that is currently in use on other transformers